## Overview
ESTIMATING SUMMARY
Endicott NY Solar Farm ¦ 525 Boswell Hill Rd, Endicott, NY 13760
Client: True Green Capital ¦ Utility: NYSEG ¦ IC File #17408 ¦ POI: 34.5 kV Feeder #8109806
CRITICAL: THREE CONFLICTING DESIGN BASES IN PACKAGE
Parameter | 2023 90% (Fixed) | 2024 Layout (SAT) | 2026 Estimate
DC Size | 7.011 MWdc | 5.026 MWp | 6.739 MWdc
AC Size | 5.0 MWac | 5.0 MW | 4.992 MWac
DC/AC Ratio | 1.40 | 1.005 | 1.35
Modules | 12,300 x 570W | 8,448 x 595W | 11,520 x 585W
Racking | Fixed tilt 25° | Solargik SAT | Fixed tilt
Inverters | 40x CPS 125kW | 16x Sungrow 312kW | 16x 312kW
Strings | N/A | 352 (24/string) | N/A
Action required: Confirm current design basis with developer before pricing. Town approved SAT revision Sept 2024, but 2026 estimate reverts to fixed tilt.
Key Project Data |  |  |  | Permitting Status
Gross Parcel | 31.68 acres; ~20 ac buildable per estimate |  |  | Permit / Approval | Status | Date
ISA Capacity | 5,000 kW nonresidential PV (executed 12/20/2021) |  |  | SEQRA Negative Declaration | Complete | 4/12/2022
IC Cost (CESIR) | $321,720 planning-grade; 25% paid 12/9/21, 75% paid 6/2/22 |  |  | ZBA Setback Variances | Complete | 5/16/2022
IC Assignment | RESunance → Endicott NY Solar Farm LLC (NYSEG consent 4/26/24) |  |  | Special Use Permit | Complete | 5/17/2022
GCR | 48% (2024 SAT layout) |  |  | Site Plan (original) | Complete | 5/17/2022
Transformers | 2x 2,650 kVA (per CESIR) |  |  | SAT Revised Site Plan Accepted | Complete | 9/10/2024
Fence | ~4,471 ft; UG MV cable ~786 ft |  |  | SHPO No-Effect | Complete | 10/20/2021
Combiners | 20 (estimate basis; not confirmed as final) |  |  | USACE Preliminary JD | Complete (non-binding) | 3/28/2022
POI Equipment | GOAB, customer/utility reclosers, metering shown on plans |  |  | FAA No-Impact | Complete | 5/5/2022
Wetlands | 3 areas, ~10.63 ac total — real layout constraint |  |  | Decommissioning / PILOT / Host Comm. | Approved by resolution | 11/6/2024
Flood Zone | Zone C, minimal |  |  | Decommissioning Bond ($175K) | Required before bldg permit | N/A
Geotech | Desktop DDR only — no field borings or pile testing found |  |  | Final SWPPP | NOT FOUND | Required pre-permit
|  |  |  | Building Permit | NOT FOUND | —
Key Risks for Estimating
1. | Design basis not frozen: Three different module counts, DC sizes, and racking types across documents. Cannot price without confirmed BOM.
2. | No field geotech: Desktop report only. Pile embedment, refusal depth, and foundation design are unresolvable without borings.
3. | No IFC drawings: 90% electrical set is 2023 fixed-tilt vintage. 2024 SAT layout is a single sheet, not a construction set.
4. | IC equipment mismatch: CESIR assumed 2x centralized inverters; current design shows 16 string inverters. Reconfirm with NYSEG.
5. | Construction permits outstanding: Building, electrical, highway access permits not evidenced. SWPPP not finalized.
6. | Owner-furnished equipment scope unclear: Pricing template suggests owner supply for modules/racking/inverters/transformers, but not confirmed.
7. | Schedule: Estimate references Q2 2026 start. No NTP, mob date, or COD milestone found in development docs.
Available Documents for Estimating
ISA, CESIR, IC assignment/consent, 90% electrical set (2023, fixed-tilt), SAT electrical layout (2024, single sheet), SAT plan with fence/MV/GCR, ALTA survey (image-based), desktop geotech DDR, Phase I ESA, wetland delineation, site analysis, civil/site plan (2022 approval vintage), EPC contract redline, pricing template, estimate workbook, B/C spec sections.
Not Found in Package
IFC civil set, IFC electrical/SLD (current), field geotech/pile testing, PVsyst, module cut sheets, final SWPPP, building/electrical/access permits, reconciled BOM, project schedule w/ milestones, CAD files, procurement matrix (owner vs. EPC furnished), warranty/workmanship requirements, capacity test specs, bonding/insurance requirements (beyond decommissioning).
Prepared by DEI Pre-Sales ¦ March 2026 ¦ Source: TGC Endicott Diligence Package

## RFP Download
Client Name | True Green Capital |  |  | Answered | 01.26.2026_Estimate_TGC_Endicot.xlsx | Estimate workbook client reference.
Job Name | Endicott NY Solar Farm |  |  | Answered | 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf | Town letter project name.
RFP Received Date | 2025-07-08 |  |  | Answered | 01.26.2026_Estimate_TGC_Endicot.xlsx
Bid Due Date | 2025-07-23 |  |  | Answered | 01.26.2026_Estimate_TGC_Endicot.xlsx |  | Subject | Sent By | Sent Date | Received Date
Address: | 525 Boswell Hill Road, Endicott, NY 13760 |  |  | Answered | 2021.08.14_Lease_Option.pdf; 2021.12.20_Interconnection_Agreement.pdf
Project Intake | Document-Based Response | Presales | Presales Engineer/Estimator | Status | Source | Date/Note
Topic | Comment | Intro | RFP Download | Status | Source | Date / Note
Engineering
DC size (Wdc) | Conflict: 7,011,000 W (2023 design); 5,026,000 Wp (2024 layout); 6,739,200 W (2026 estimate) | X |  | Needs Review | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 01.26.2026_Estimate_TGC_Endicot.xlsx
AC Size (Wac) | 5,000,000 W nominal; estimate basis 4,992,000 W | X |  | Partial | 2021.12.20_Interconnection_Agreement.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 01.26.2026_Estimate_TGC_Endicot.xlsx
DC/AC Ratio | Conflict: 1.40 (2023 design) vs 1.005 (2024 layout) | X |  | Needs Review | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Type of System (FT/SAT/Ballasted) | Original fixed tilt; revised and currently reflected as single-axis tracker | X |  | Answered | 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Tracker Power? | AC powered tracker shown in bid RFQ; project layout confirms SAT but not power architecture in permit drawings |  | X | Partial | VendorSubContractor RFQ; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Design Life? | Not found |  | X | Not Found
Module Clearance | Not found |  | X | Not Found
Is there a layout available? | Yes - Town site plan, 2023 90% design, and 2024 electrical site layout are all present |  | X | Answered | 2022.04.12_Site_Plan.pdf; 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Tilt/Azimuth | 2023 fixed tilt 25 deg; 2024 SAT layout +/-60 deg tracker, azimuth 0 deg |  | X | Partial | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
GCR | 48% in current SAT layout |  | X | Answered | 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Interconnection Utility | NYSEG |  | X | Answered | 2021.12.20_Interconnection_Agreement.pdf
Interconnection Voltage | 34.5 kV |  | X | Answered | 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 2022.01.11_CESIR_REV1.pdf
Inverter/Secondary Voltage | 0.6 kV on CESIR basis |  | X | Partial | 2022.01.11_CESIR_REV1.pdf
Module Type/s | Conflict: Qcells 570 W; Qcells 595 W; estimate basis 585 W |  | X | Needs Review | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 01.26.2026_Estimate_TGC_Endicot.xlsx
Total Modules | Conflict: 12,300; 8,448; 11,520 |  | X | Needs Review | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 01.26.2026_Estimate_TGC_Endicot.xlsx
Modules /String | 24 in latest SAT layout |  | X | Answered | 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Total # of Piles/Screws | Not found |  | X | Not Found
Is there a PV Syst available? | Not found |  | X | Not Found
Is DEI Engineering for the Bid? | Not evidenced in diligence package | X |  | Not Found
Geotech Available? | Desktop due diligence report present; field geotech/borings not found |  | X | Partial | 231120_FULL_DDR_ENDICOTT__29_ACRES_BROOME_COUNTY_V1.pdf
Refusal Strategy? | Not found |  | X | Not Found
CESIR (Impact Study) Available? | Yes |  | X | Answered | 2022.01.11_CESIR_REV1.pdf | 2022-01-11
ISA Available? | Yes |  | X | Answered | 2021.12.20_Interconnection_Agreement.pdf | 2021-12-20
Warranty Requirements | Not found project-specifically |  | X | Not Found
Workmanship | Not found project-specifically |  | X | Not Found
Racking | Conflict: older fixed tilt design vs current Solargik SAT layout |  | X | Needs Review | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Inverter | Conflict: 40x CPS125KTL vs 16x SG350HX |  | X | Needs Review | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Any other equipment? | 2 transformers; POI metering, recloser, cutout, customer AC disconnect shown |  | X | Partial | 2022.01.11_CESIR_REV1.pdf; Endicott_1.0_04082024-SAT_48GCR-E-100.pdf
X
Equipment:
Module cut sheet | Not found in package |  | X | Not Found
Racking | Conflict: older fixed tilt design vs current Solargik SAT layout |  | X | Needs Review | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Inverter | Conflict: 40x CPS125KTL vs 16x SG350HX |  | X | Needs Review | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Any AC or DC disconnects for the inverters | Customer AC disconnect shown at POI; inverter-level DC/AC disconnect details not fully confirmed |  | X | Partial | Endicott_1.0_04082024-SAT_48GCR-E-100.pdf
Combiner Boxes | 20 combiner boxes in estimate basis; final design quantity not confirmed |  | X | Partial | 01.26.2026_Estimate_TGC_Endicot.xlsx
Switchboard | Not clearly identified |  | X | Not Found
Control Power/Aux Power | Not found |  | X | Not Found
MV Transformers | 2 x 2650 kVA in CESIR basis |  | X | Answered | 2022.01.11_CESIR_REV1.pdf
LV GXFMR | Not found |  | X | Not Found
MV GXFMR/NGR | Not found |  | X | Not Found
GOAB | Shown in SAT plan |  | X | Answered | Endicott_1.0_04082024-SAT_48GCR-E-100.pdf
Recloser | Utility and customer reclosers shown in SAT plan / latest layout |  | X | Answered | Endicott_1.0_04082024-SAT_48GCR-E-100.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Metering Cluster + Meter | Customer and utility metering shown at POI |  | X | Partial | Endicott_1.0_04082024-SAT_48GCR-E-100.pdf
Pad Mount Switchgear | Not found clearly |  | X | Not Found
DAS | Shown in latest layout symbols / communications basis |  | X | Partial | 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Permit:
What all permitting is required/available | Town SEQRA/variance/SUP/site plan; SHPO; FAA; USACE preliminary JD; USFWS species list; decommissioning/stormwater/PILOT/host community docs | X |  | Answered | multiple permitting docs
1. Town | Variance approved 2022-05-16; SUP and site plan approved 2022-05-17; tracker revision accepted 2024-09-10 |  | X | Answered | 2022.05.16_Variance_Approval_FE.pdf; 2022.05.19_Special_Use_Permit_Letter_FE.pdf; 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
2. County | 239-M review file present; county filing receipt required for maintenance agreement/access easement before building permit |  | X | Partial | 2022.04.04_239-M_Review.pdf; 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
3. State | SHPO no effect; SEQRA negative declaration; stormwater/SPDES framework referenced |  | X | Partial | 2021.10.20_SHPO_No_Effect_Letter.pdf; 2022.04.12_EAF.pdf
4. Federal | USACE preliminary JD; FAA letter; USFWS species list |  | X | Answered | 2022.03.28_Preliminary_JD.pdf; 2022.05.05_FAA_No_Impact_Letter.pdf; 2024.03.28_USFWS_Engandered_Species_List.pdf
SWPPP | Required and must be finalized prior to building permit; final approval not found |  | X | Partial | 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
Building Permit | Not found |  | X | Not Found
Electrical Permit | Not found |  | X | Not Found
Entrance Permit | Highway permit required for access drive; issuance not found |  | X | Partial | 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
1. Local | Town of Union approvals as above |  | X | Answered | Town approval docs
2. DOT? | Local highway permit required; DOT permit not evidenced |  | X | Partial | 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
Any Wetlands? | Yes - 3 wetlands totaling approx. 10.63 acres identified |  | X | Answered | 2021.11.05_Project_Site_Analysis.pdf; 2021.12.06_Wetland_Delineation_(optimized).pdf
FEMA/Flood Risk? | Zone C / minimal flooding per site analysis |  | X | Answered | 2021.11.05_Project_Site_Analysis.pdf
Drawings
Civil Drawings | Present |  | X | Answered | 2022.04.12_Site_Plan.pdf
1. PDF | Yes |  | X | Answered | site plan/design PDFs
2. CAD | Not found in package |  | X | Not Found
3. Topo and ALTA available? | ALTA survey present; topo not separately verified |  | X | Partial | 2024.04.20_ALTA_Survey.pdf
Electrical Drawings | Present |  | X | Answered | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Client Documents/Requirements:
Owner Provided Equipment? | Bid materials suggest owner supply for modules, racking, inverters, transformers; not confirmed as executed term | X |  | Partial | Pricing Template - December 2025 (DEI).xlsx
Client EPC available? | Redline EPC form present; not executed | X |  | Partial | 2025-4-28 UGE - EPC Co to SubContractor Agreement - DEI Redline.docx
Capacity Gaurantee/PF Test requirements? | Not found project-specifically |  | X | Not Found
Total Limit of Liability requirements? | Not found project-specifically |  | X | Not Found
Additional Client Requirements
Client Approved Vendor List Available | Not found | X |  | Not Found
IRA required? | IRA-compliant labor referenced in proposal; binding project requirement not confirmed | X |  | Partial | 02.25.2026_V4 Proposal_UGEI Portfolio.pdf
Domestic Content Required? | Optional adder in bid materials; not confirmed as owner requirement | X |  | Partial | VendorSubContractor RFQ
Sales Tax Exempt? | Yes in bid materials | X |  | Partial | VendorSubContractor RFQ; Pricing Template - December 2025 (DEI).xlsx
Schedule requirements | Estimate shows Start Date Q2 2026; fixed PPA / COD milestone not found in diligence docs | X |  | Partial | 01.26.2026_Estimate_TGC_Endicot.xlsx
RFP Schedule | Not found | X |  | Not Found
# of Bidders | Not found | X |  | Not Found
Price Target | Not found | X |  | Not Found
EPC Execution Date? | Not found | X |  | Not Found
Mob Date? | 2025-09-01 in vendor RFQ sheet |  | X | Partial | VendorSubContractor RFQ
MC? | Not found |  | X | Not Found
SC? | Not found |  | X | Not Found
Interconnection date from the ISA? | ISA dated 2021-12-20; project in-service/COD milestone not clearly found |  | X | Partial | 2021.12.20_Interconnection_Agreement.pdf
Client Financing | Not found | X |  | Not Found
Any RFP instructions? Add below this line for proposal requirements. | See VendorSubContractor RFQ tab for schedule/doc assumptions; no separate owner RFP instruction set found |  |  | Partial | VendorSubContractor RFQ
Bond Required? | Decommissioning bond required before building permit/start of construction; initial amount $175,000 |  |  | Answered | 2024.11.06_Decommissioning_Agreement_FE.pdf
Tarrif Risk | Not found |  |  | Not Found
FEOC Risk | Not found |  |  | Not Found
Weather Risk | Not found |  |  | Not Found
Change of Law Risk | Not found |  |  | Not Found
CashFlow/SOV requirements | Not found |  |  | Not Found
Note on B1: Status: Answered Source: 01.26.2026_Estimate_TGC_Endicot.xlsx Estimate workbook client reference.
Note on B2: Status: Answered Source: 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf Town letter project name.
Note on B3: Status: Answered Source: 01.26.2026_Estimate_TGC_Endicot.xlsx
Note on B4: Status: Answered Source: 01.26.2026_Estimate_TGC_Endicot.xlsx
Note on B5: Status: Answered Source: 2021.08.14_Lease_Option.pdf; 2021.12.20_Interconnection_Agreement.pdf
Note on B9: Status: Needs Review Source: 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 01.26.2026_Estimate_TGC_Endicot.xlsx
Note on B10: Status: Partial Source: 2021.12.20_Interconnection_Agreement.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 01.26.2026_Estimate_TGC_Endicot.xlsx
Note on B11: Status: Needs Review Source: 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Note on B12: Status: Answered Source: 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Note on B13: Status: Partial Source: VendorSubContractor RFQ; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Note on B14: Status: Not Found Source: Not found in reviewed docs
Note on B15: Status: Not Found Source: Not found in reviewed docs
Note on B16: Status: Answered Source: 2022.04.12_Site_Plan.pdf; 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Note on B17: Status: Partial Source: 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Note on B18: Status: Answered Source: 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Note on B19: Status: Answered Source: 2021.12.20_Interconnection_Agreement.pdf
Note on B20: Status: Answered Source: 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 2022.01.11_CESIR_REV1.pdf
Note on B21: Status: Partial Source: 2022.01.11_CESIR_REV1.pdf
Note on B22: Status: Needs Review Source: 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 01.26.2026_Estimate_TGC_Endicot.xlsx
Note on B23: Status: Needs Review Source: 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 01.26.2026_Estimate_TGC_Endicot.xlsx
Note on B24: Status: Answered Source: 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Note on B25: Status: Not Found Source: Not found in reviewed docs
Note on B26: Status: Not Found Source: Not found in reviewed docs
Note on B27: Status: Not Found Source: Not found in reviewed docs
Note on A28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Add additional points here
Note on B28: Status: Partial Source: 231120_FULL_DDR_ENDICOTT__29_ACRES_BROOME_COUNTY_V1.pdf
Note on B29: Status: Not Found Source: Not found in reviewed docs
Note on B30: Status: Answered Source: 2022.01.11_CESIR_REV1.pdf 2022-01-11
Note on B31: Status: Answered Source: 2021.12.20_Interconnection_Agreement.pdf 2021-12-20
Note on B32: Status: Not Found Source: Not found in reviewed docs
Note on B33: Status: Not Found Source: Not found in reviewed docs
Note on B34: Status: Needs Review Source: 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Note on B35: Status: Needs Review Source: 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Note on B36: Status: Partial Source: 2022.01.11_CESIR_REV1.pdf; Endicott_1.0_04082024-SAT_48GCR-E-100.pdf
Note on B39: Status: Not Found Source: Not found in reviewed docs
Note on B40: Status: Needs Review Source: 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Note on B41: Status: Needs Review Source: 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Note on B42: Status: Partial Source: Endicott_1.0_04082024-SAT_48GCR-E-100.pdf
Note on B43: Status: Partial Source: 01.26.2026_Estimate_TGC_Endicot.xlsx
Note on B44: Status: Not Found Source: Not found in reviewed docs
Note on B45: Status: Not Found Source: Not found in reviewed docs
Note on B46: Status: Answered Source: 2022.01.11_CESIR_REV1.pdf
Note on B47: Status: Not Found Source: Not found in reviewed docs
Note on B48: Status: Not Found Source: Not found in reviewed docs
Note on B49: Status: Answered Source: Endicott_1.0_04082024-SAT_48GCR-E-100.pdf
Note on B50: Status: Answered Source: Endicott_1.0_04082024-SAT_48GCR-E-100.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Note on B51: Status: Partial Source: Endicott_1.0_04082024-SAT_48GCR-E-100.pdf
Note on B52: Status: Not Found Source: Not found in reviewed docs
Note on B53: Status: Partial Source: 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Note on B56: Status: Answered Source: multiple permitting docs
Note on B57: Status: Answered Source: 2022.05.16_Variance_Approval_FE.pdf; 2022.05.19_Special_Use_Permit_Letter_FE.pdf; 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
Note on B58: Status: Partial Source: 2022.04.04_239-M_Review.pdf; 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
Note on B59: Status: Partial Source: 2021.10.20_SHPO_No_Effect_Letter.pdf; 2022.04.12_EAF.pdf
Note on B60: Status: Answered Source: 2022.03.28_Preliminary_JD.pdf; 2022.05.05_FAA_No_Impact_Letter.pdf; 2024.03.28_USFWS_Engandered_Species_List.pdf
Note on B61: Status: Partial Source: 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
Note on B62: Status: Not Found Source: Not found in reviewed docs
Note on B63: Status: Not Found Source: Not found in reviewed docs
Note on B64: Status: Partial Source: 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
Note on B65: Status: Answered Source: Town approval docs
Note on B66: Status: Partial Source: 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
Note on B67: Status: Answered Source: 2021.11.05_Project_Site_Analysis.pdf; 2021.12.06_Wetland_Delineation_(optimized).pdf
Note on B68: Status: Answered Source: 2021.11.05_Project_Site_Analysis.pdf
Note on B71: Status: Answered Source: 2022.04.12_Site_Plan.pdf
Note on B72: Status: Answered Source: site plan/design PDFs
Note on B73: Status: Not Found Source: Not found in reviewed docs
Note on B74: Status: Partial Source: 2024.04.20_ALTA_Survey.pdf
Note on B75: Status: Answered Source: 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Note on B78: Status: Partial Source: Pricing Template - December 2025 (DEI).xlsx
Note on B79: Status: Partial Source: 2025-4-28 UGE - EPC Co to SubContractor Agreement - DEI Redline.docx
Note on B80: Status: Not Found Source: Not found in reviewed docs
Note on B81: Status: Not Found Source: Not found in reviewed docs
Note on B83: Status: Not Found Source: Not found in reviewed docs
Note on B84: Status: Partial Source: 02.25.2026_V4 Proposal_UGEI Portfolio.pdf
Note on B85: Status: Partial Source: VendorSubContractor RFQ
Note on B86: Status: Partial Source: VendorSubContractor RFQ; Pricing Template - December 2025 (DEI).xlsx
Note on B87: Status: Partial Source: 01.26.2026_Estimate_TGC_Endicot.xlsx
Note on B88: Status: Not Found Source: Not found in reviewed docs
Note on B89: Status: Not Found Source: Not found in reviewed docs
Note on B90: Status: Not Found Source: Not found in reviewed docs
Note on B91: Status: Not Found Source: Not found in reviewed docs
Note on B92: Status: Partial Source: VendorSubContractor RFQ
Note on B93: Status: Not Found Source: Not found in reviewed docs
Note on B94: Status: Not Found Source: Not found in reviewed docs
Note on B95: Status: Partial Source: 2021.12.20_Interconnection_Agreement.pdf
Note on B96: Status: Not Found Source: Not found in reviewed docs
Note on B98: Status: Partial Source: VendorSubContractor RFQ
Note on B99: Status: Answered Source: 2024.11.06_Decommissioning_Agreement_FE.pdf
Note on B100: Status: Not Found Source: Not found in reviewed docs
Note on B101: Status: Not Found Source: Not found in reviewed docs
Note on B102: Status: Not Found Source: Not found in reviewed docs
Note on B103: Status: Not Found Source: Not found in reviewed docs
Note on B104: Status: Not Found Source: Not found in reviewed docs

## Diligence Matrix
Field Name | Extracted Answer | Status | Source Document | Date / Note
Client Name | True Green Capital | Answered | 01.26.2026_Estimate_TGC_Endicot.xlsx | Estimate workbook client reference.
Job Name | Endicott NY Solar Farm | Answered | 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf | Town letter project name.
RFP Received Date | 2025-07-08 | Answered | 01.26.2026_Estimate_TGC_Endicot.xlsx
Bid Due Date | 2025-07-23 | Answered | 01.26.2026_Estimate_TGC_Endicot.xlsx
Address: | 525 Boswell Hill Road, Endicott, NY 13760 | Answered | 2021.08.14_Lease_Option.pdf; 2021.12.20_Interconnection_Agreement.pdf
DC size (Wdc) | Conflict: 7,011,000 W (2023 design); 5,026,000 Wp (2024 layout); 6,739,200 W (2026 estimate) | Needs Review | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 01.26.2026_Estimate_TGC_Endicot.xlsx
AC Size (Wac) | 5,000,000 W nominal; estimate basis 4,992,000 W | Partial | 2021.12.20_Interconnection_Agreement.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 01.26.2026_Estimate_TGC_Endicot.xlsx
DC/AC Ratio | Conflict: 1.40 (2023 design) vs 1.005 (2024 layout) | Needs Review | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Type of System (FT/SAT/Ballasted) | Original fixed tilt; revised and currently reflected as single-axis tracker | Answered | 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Tracker Power? | AC powered tracker shown in bid RFQ; project layout confirms SAT but not power architecture in permit drawings | Partial | VendorSubContractor RFQ; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Design Life? | Not found | Not Found
Module Clearance | Not found | Not Found
Is there a layout available? | Yes - Town site plan, 2023 90% design, and 2024 electrical site layout are all present | Answered | 2022.04.12_Site_Plan.pdf; 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Tilt/Azimuth | 2023 fixed tilt 25 deg; 2024 SAT layout +/-60 deg tracker, azimuth 0 deg | Partial | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
GCR | 48% in current SAT layout | Answered | 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Interconnection Utility | NYSEG | Answered | 2021.12.20_Interconnection_Agreement.pdf
Interconnection Voltage | 34.5 kV | Answered | 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 2022.01.11_CESIR_REV1.pdf
Inverter/Secondary Voltage | 0.6 kV on CESIR basis | Partial | 2022.01.11_CESIR_REV1.pdf
Module Type/s | Conflict: Qcells 570 W; Qcells 595 W; estimate basis 585 W | Needs Review | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 01.26.2026_Estimate_TGC_Endicot.xlsx
Total Modules | Conflict: 12,300; 8,448; 11,520 | Needs Review | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf; 01.26.2026_Estimate_TGC_Endicot.xlsx
Modules /String | 24 in latest SAT layout | Answered | 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Total # of Piles/Screws | Not found | Not Found
Is there a PV Syst available? | Not found | Not Found
Is DEI Engineering for the Bid? | Not evidenced in diligence package | Not Found
Geotech Available? | Desktop due diligence report present; field geotech/borings not found | Partial | 231120_FULL_DDR_ENDICOTT__29_ACRES_BROOME_COUNTY_V1.pdf
Refusal Strategy? | Not found | Not Found
CESIR (Impact Study) Available? | Yes | Answered | 2022.01.11_CESIR_REV1.pdf | 2022-01-11
ISA Available? | Yes | Answered | 2021.12.20_Interconnection_Agreement.pdf | 2021-12-20
Warranty Requirements | Not found project-specifically | Not Found
Workmanship | Not found project-specifically | Not Found
Racking | Conflict: older fixed tilt design vs current Solargik SAT layout | Needs Review | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Inverter | Conflict: 40x CPS125KTL vs 16x SG350HX | Needs Review | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Any other equipment? | 2 transformers; POI metering, recloser, cutout, customer AC disconnect shown | Partial | 2022.01.11_CESIR_REV1.pdf; Endicott_1.0_04082024-SAT_48GCR-E-100.pdf
Module cut sheet | Not found in package | Not Found
Any AC or DC disconnects for the inverters | Customer AC disconnect shown at POI; inverter-level DC/AC disconnect details not fully confirmed | Partial | Endicott_1.0_04082024-SAT_48GCR-E-100.pdf
Combiner Boxes | 20 combiner boxes in estimate basis; final design quantity not confirmed | Partial | 01.26.2026_Estimate_TGC_Endicot.xlsx
Switchboard | Not clearly identified | Not Found
Control Power/Aux Power | Not found | Not Found
MV Transformers | 2 x 2650 kVA in CESIR basis | Answered | 2022.01.11_CESIR_REV1.pdf
LV GXFMR | Not found | Not Found
MV GXFMR/NGR | Not found | Not Found
GOAB | Shown in SAT plan | Answered | Endicott_1.0_04082024-SAT_48GCR-E-100.pdf
Recloser | Utility and customer reclosers shown in SAT plan / latest layout | Answered | Endicott_1.0_04082024-SAT_48GCR-E-100.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Metering Cluster + Meter | Customer and utility metering shown at POI | Partial | Endicott_1.0_04082024-SAT_48GCR-E-100.pdf
Pad Mount Switchgear | Not found clearly | Not Found
DAS | Shown in latest layout symbols / communications basis | Partial | 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
What all permitting is required/available | Town SEQRA/variance/SUP/site plan; SHPO; FAA; USACE preliminary JD; USFWS species list; decommissioning/stormwater/PILOT/host community docs | Answered | multiple permitting docs
1. Town | Variance approved 2022-05-16; SUP and site plan approved 2022-05-17; tracker revision accepted 2024-09-10 | Answered | 2022.05.16_Variance_Approval_FE.pdf; 2022.05.19_Special_Use_Permit_Letter_FE.pdf; 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
2. County | 239-M review file present; county filing receipt required for maintenance agreement/access easement before building permit | Partial | 2022.04.04_239-M_Review.pdf; 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
3. State | SHPO no effect; SEQRA negative declaration; stormwater/SPDES framework referenced | Partial | 2021.10.20_SHPO_No_Effect_Letter.pdf; 2022.04.12_EAF.pdf
4. Federal | USACE preliminary JD; FAA letter; USFWS species list | Answered | 2022.03.28_Preliminary_JD.pdf; 2022.05.05_FAA_No_Impact_Letter.pdf; 2024.03.28_USFWS_Engandered_Species_List.pdf
SWPPP | Required and must be finalized prior to building permit; final approval not found | Partial | 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
Building Permit | Not found | Not Found
Electrical Permit | Not found | Not Found
Entrance Permit | Highway permit required for access drive; issuance not found | Partial | 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
1. Local | Town of Union approvals as above | Answered | Town approval docs
2. DOT? | Local highway permit required; DOT permit not evidenced | Partial | 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
Any Wetlands? | Yes - 3 wetlands totaling approx. 10.63 acres identified | Answered | 2021.11.05_Project_Site_Analysis.pdf; 2021.12.06_Wetland_Delineation_(optimized).pdf
FEMA/Flood Risk? | Zone C / minimal flooding per site analysis | Answered | 2021.11.05_Project_Site_Analysis.pdf
Civil Drawings | Present | Answered | 2022.04.12_Site_Plan.pdf
1. PDF | Yes | Answered | site plan/design PDFs
2. CAD | Not found in package | Not Found
3. Topo and ALTA available? | ALTA survey present; topo not separately verified | Partial | 2024.04.20_ALTA_Survey.pdf
Electrical Drawings | Present | Answered | 230816_ENDICOTT_90%_DESIGN_R1.pdf; 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf
Owner Provided Equipment? | Bid materials suggest owner supply for modules, racking, inverters, transformers; not confirmed as executed term | Partial | Pricing Template - December 2025 (DEI).xlsx
Client EPC available? | Redline EPC form present; not executed | Partial | 2025-4-28 UGE - EPC Co to SubContractor Agreement - DEI Redline.docx
Capacity Gaurantee/PF Test requirements? | Not found project-specifically | Not Found
Total Limit of Liability requirements? | Not found project-specifically | Not Found
Client Approved Vendor List Available | Not found | Not Found
IRA required? | IRA-compliant labor referenced in proposal; binding project requirement not confirmed | Partial | 02.25.2026_V4 Proposal_UGEI Portfolio.pdf
Domestic Content Required? | Optional adder in bid materials; not confirmed as owner requirement | Partial | VendorSubContractor RFQ
Sales Tax Exempt? | Yes in bid materials | Partial | VendorSubContractor RFQ; Pricing Template - December 2025 (DEI).xlsx
Schedule requirements | Estimate shows Start Date Q2 2026; fixed PPA / COD milestone not found in diligence docs | Partial | 01.26.2026_Estimate_TGC_Endicot.xlsx
RFP Schedule | Not found | Not Found
# of Bidders | Not found | Not Found
Price Target | Not found | Not Found
EPC Execution Date? | Not found | Not Found
Mob Date? | 2025-09-01 in vendor RFQ sheet | Partial | VendorSubContractor RFQ
MC? | Not found | Not Found
SC? | Not found | Not Found
Interconnection date from the ISA? | ISA dated 2021-12-20; project in-service/COD milestone not clearly found | Partial | 2021.12.20_Interconnection_Agreement.pdf
Client Financing | Not found | Not Found
Any RFP instructions? Add below this line for proposal requirements. | See VendorSubContractor RFQ tab for schedule/doc assumptions; no separate owner RFP instruction set found | Partial | VendorSubContractor RFQ
Bond Required? | Decommissioning bond required before building permit/start of construction; initial amount $175,000 | Answered | 2024.11.06_Decommissioning_Agreement_FE.pdf
Tarrif Risk | Not found | Not Found
FEOC Risk | Not found | Not Found
Weather Risk | Not found | Not Found
Change of Law Risk | Not found | Not Found
CashFlow/SOV requirements | Not found | Not Found

## Permit Timeline
Date | Milestone | Status | Responsible Party | Source Document
2021-10-20 | SHPO no-effect finding issued | Complete | Applicant / SHPO | 2021.10.20_SHPO_No_Effect_Letter.pdf
2021-12-06 | Wetland delineation report issued (fieldwork 2021-10-01) | Complete | Delta / project team | 2021.12.06_Wetland_Delineation_(optimized).pdf
2022-03-28 | USACE preliminary JD issued | Complete | USACE / applicant | 2022.03.28_Preliminary_JD.pdf
2022-04-12 | Planning Board approved Negative Declaration under SEQRA | Complete | Town of Union Planning Board | 2022.05.19_Special_Use_Permit_Letter_FE.pdf
2022-05-05 | FAA no-impact / no-hazard letter | Complete | FAA / applicant | 2022.05.05_FAA_No_Impact_Letter.pdf
2022-05-16 | ZBA setback variances approved | Complete | Town of Union ZBA | 2022.05.16_Variance_Approval_FE.pdf
2022-05-17 | Special use permit approved | Complete | Town of Union Planning Board | 2022.05.19_Special_Use_Permit_Letter_FE.pdf
2022-05-17 | Site plan approved with stipulations | Complete | Town of Union Planning Board | 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
2024-09-10 | Planning Board accepted revised tracker site plan | Complete | Town of Union Planning Board | 2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf
2024-11-06 | Town Board approved decommissioning/stormwater/host community/PILOT agreements | Approved by resolution | Town of Union | 2024.11.06_TOU_Approvals_Resolution_FE.pdf
2026-02-05 | Town planner confirms no re-approval needed for original site plan basis | Confirmatory correspondence | Town of Union Planning | Endicott_Town_Planner_approval_email_on_revised_fixed_tilt_site_plan_2.5.26.pdf

## Quantities
Quantity | Value | Source Document | Notes
AC capacity | 5.0 MWac | 2021.12.20_Interconnection_Agreement.pdf | ISA basis
AC capacity | 5.0 MWac | 230816_ENDICOTT_90%_DESIGN_R1.pdf | 2023 design basis
AC capacity | 4.992 MWac | 01.26.2026_Estimate_TGC_Endicot.xlsx | Estimate basis
DC capacity | 7.011 MWdc | 230816_ENDICOTT_90%_DESIGN_R1.pdf | Fixed-tilt basis
DC capacity | 5.026 MWp | 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf | Current SAT basis
DC capacity | 6.7392 MWdc | 01.26.2026_Estimate_TGC_Endicot.xlsx | Estimate basis
Gross parcel acreage | 31.68 acres | 2021.08.14_Lease_Option.pdf | Property description
Lease parcel area | 16.99 acres | 2024.12.10_Phase_I_ESA_-_Endicott.pdf | ESA
Buildable area | 20 acres | 01.26.2026_Estimate_TGC_Endicot.xlsx | Estimate assumption
Modules | 12,300 x 570W | 230816_ENDICOTT_90%_DESIGN_R1.pdf | Qcells G11.3
Modules | 8,448 x 595W | 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf | Qcells G11S
Modules | 11,520 x 585W | 01.26.2026_Estimate_TGC_Endicot.xlsx | Estimate basis
Modules per string | 24 | 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf | SAT basis
Strings | 352 | 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf | SAT basis
Inverters | 40 x CPS125KTL | 230816_ENDICOTT_90%_DESIGN_R1.pdf | Old basis
Inverters | 16 x SG350HX | 2024.10.24_Electrical_Site_Layout_-_Endicott.pdf | Current basis
Transformers | 2 x 2650 kVA | 2022.01.11_CESIR_REV1.pdf | CESIR basis
Fence length | ~4,471 ft | Endicott_1.0_04082024-SAT_48GCR-E-100.pdf | Plan note
UG MV cable | ~786 ft | Endicott_1.0_04082024-SAT_48GCR-E-100.pdf | Plan note

## Document Inventory
Label Name | Type | Folder Path | Category
01.26.2026_Estimate_TGC_Endicot.xlsx | XLSX | Sales Automation/Take Off, Estimate | Financial
02.25.2026_V4 Proposal_UGEI Portfolio.pdf | PDF | Sales Automation/Proposal | Contracts / Commercial
2021.03.01_Appendix_H_Property_Owner_Consent.pdf | PDF | Sales Automation/Client Data Transfer/Documents/05-Interconnection/Application | Interconnection
2021.03.01_Appendix_J_Site_Control_Consent.pdf | PDF | Sales Automation/Client Data Transfer/Documents/05-Interconnection/Application | Interconnection
2021.03.29_Preliminary_Screening.pdf | PDF | Sales Automation/Client Data Transfer/Documents/05-Interconnection/Study | Interconnection
2021.08.14_Lease_Option.pdf | PDF | Sales Automation/Client Data Transfer/Documents/02-Internal-Only/Site-Control/Lease-Agreement | Site Control
2021.10.20_SHPO_No_Effect_Letter.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
2021.11.05_Project_Site_Analysis.pdf | PDF | Sales Automation/Client Data Transfer/Documents/07-Engineering/Consultant-Reports | Other
2021.12.06_Wetland_Delineation_(optimized).pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
2021.12.06_Wetlands_Delineation.pdf | PDF | Sales Automation/Client Data Transfer/Documents/07-Engineering/Consultant-Reports | Environmental
2021.12.20_Interconnection_Agreement.pdf | PDF | Sales Automation/Client Data Transfer/Documents/05-Interconnection/Agreements | Interconnection
2022.01.11_CESIR_REV1.pdf | PDF | Sales Automation/Client Data Transfer/Documents/05-Interconnection/CESIR | Interconnection
2022.03.28_Preliminary_JD.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval/Local-Approval-Set-and-Submissions-(SUP) | Interconnection
2022.04.04_239-M_Review.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
2022.04.12_EAF.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
2022.04.12_Site_Plan.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval/Local-Approval-Set-and-Submissions-(SUP) | Interconnection
2022.04.12_Site_Visualizations_-_Endicott.pdf | PDF | Sales Automation/Client Data Transfer/Documents/07-Engineering/Consultant-Reports | Other
2022.04.26_Sketch_Plan.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval/Local-Approval-Set-and-Submissions-(SUP) | Interconnection
2022.05.05_FAA_No_Impact_Letter.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
2022.05.05_FAA_No_Impact_Letter.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval/Local-Approval-Set-and-Submissions-(SUP) | Interconnection
2022.05.16_Variance_Approval_FE.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
2022.05.17_Site_Plan_-_Signed_-_Endicott.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval/Local-Approval-Set-and-Submissions-(SUP) | Interconnection
2022.05.19_Special_Use_Permit_Letter_FE.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
2022.06.02_75%_Payment_Confirmation.pdf | PDF | Sales Automation/Client Data Transfer/Documents/05-Interconnection/Corrispondence | Interconnection
2023.02.06_Deed.pdf | PDF | Sales Automation/Client Data Transfer/Documents/02-Internal-Only/Site-Control | Site Control
2023.06.09_NYSEG_Easement.pdf | PDF | Sales Automation/Client Data Transfer/Documents/02-Internal-Only/Site-Control/Easements | Site Control
2023.06.26_Lease_Option_Extension_Notification.pdf | PDF | Sales Automation/Client Data Transfer/Documents/02-Internal-Only/Site-Control/Lease-Agreement | Site Control
2024.03.28_USFWS_Engandered_Species_List.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
2024.04.05_Interconnection_Assignment.pdf | PDF | Sales Automation/Client Data Transfer/Documents/05-Interconnection/Corrispondence | Interconnection
2024.04.20_ALTA_Survey.pdf | PDF | Sales Automation/Client Data Transfer/Documents/07-Engineering/ALTA | Survey
2024.04.23_25%_Payment_Date.pdf | PDF | Sales Automation/Client Data Transfer/Documents/05-Interconnection/Corrispondence | Interconnection
2024.04.26_DER_Registration_Compliance_Form.pdf | PDF | Sales Automation/Client Data Transfer/Documents/05-Interconnection/Corrispondence | Interconnection
2024.04.26_Interconnection_Assignment_Consent.pdf | PDF | Sales Automation/Client Data Transfer/Documents/05-Interconnection/Corrispondence | Interconnection
2024.05.06_Title_Report.pdf | PDF | Sales Automation/Client Data Transfer/Documents/02-Internal-Only/Site-Control/Title | Site Control
2024.06.28_First_Amendment_to_Solar_Lease_Option.pdf | PDF | Sales Automation/Client Data Transfer/Documents/02-Internal-Only/Site-Control/Lease-Agreement | Site Control
2024.06.28_First_Amendment_to_Solar_Real_Estate_Lease_Option_Agreement_and_Form_Lease_Agreement_-_Endicott.pdf | PDF | Sales Automation/Client Data Transfer/Documents/02-Internal-Only/Site-Control/Lease-Agreement | Site Control
2024.10.17_Town_of_Union_Site_Plan_Approval_Letter_-_Endicott.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
2024.10.24_Electrical_Site_Layout_-_Endicott.pdf | PDF | Sales Automation/Client Data Transfer/Documents/07-Engineering/Design-and-Engineering | Electrical Design
2024.11.06_Decommissioning_Agreement_FE.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
2024.11.06_Host_Community_Agreement_-_TOUX.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
2024.11.06_PILOT_Alternative_-_Endicott1.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval/PILOT | Interconnection
2024.11.06_PILOT_Alternative_FE.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
2024.11.06_Stormwater_Maintenance_Agreement_-_Endicott.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
2024.11.06_TOU_Approvals_Resolution_FE.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
2024.11.26_TGC_-_Resunance_-_Landowner_Estoppel_-_Endicott.pdf | PDF | Sales Automation/Client Data Transfer/Documents/02-Internal-Only/Site-Control/Lease-Agreement | Site Control
2024.12.10_Phase_I_ESA_-_Endicott.pdf | PDF | Sales Automation/Client Data Transfer/Documents/07-Engineering/Consultant-Reports | Environmental
2025-4-28 UGE - EPC Co to SubContractor Agreement - DEI Redline.docx | DOCX | Sales Automation/EPC Contract | Contracts / Commercial
230816_ENDICOTT_90%_DESIGN_R1.pdf | PDF | Sales Automation/Client Data Transfer/Documents/07-Engineering/Design-and-Engineering/90%-DESIGN | Other
231120_FULL_DDR_ENDICOTT__29_ACRES_BROOME_COUNTY_V1.pdf | PDF | Sales Automation/Client Data Transfer/Documents/07-Engineering/Consultant-Reports | Geotechnical
B-0-Technical-Specifications_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/B--Technical-Specifications | Contracts / Commercial
B-1-PV-Modules-Technical-Specification_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/B--Technical-Specifications | Contracts / Commercial
B-10-ACSS-AW-Conductor-Specification_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/B--Technical-Specifications | Contracts / Commercial
B-11-Insulator-Specification_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/B--Technical-Specifications | Contracts / Commercial
B-12-SCADA-System-Specification_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/B--Technical-Specifications | Contracts / Commercial
B-13-Combiner-and-DC-Disconnect-Specifications_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/B--Technical-Specifications | Contracts / Commercial
B-2-Inverter-Specification_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/B--Technical-Specifications | Contracts / Commercial
B-3-MV-Transformer-Specification_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/B--Technical-Specifications | Contracts / Commercial
B-4-Racking-Single-Axis-Tacker-Specification_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/B--Technical-Specifications | Contracts / Commercial
B-5-LV-Cabling-Technical-Specification_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/B--Technical-Specifications | Contracts / Commercial
B-6-Cable-Specifications_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/B--Technical-Specifications | Contracts / Commercial
B-7-MV-J-Box-Specification_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/B--Technical-Specifications | Contracts / Commercial
B-8-Wood-Pole-Specification_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/B--Technical-Specifications | Contracts / Commercial
B-9-ADSS-Fiber-Optic-Cable-Specification_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/B--Technical-Specifications | Contracts / Commercial
Bid Info Template.xlsx | XLSX | Uploaded separately | Other
C-0-Major-Installation-&-Construction-Specifications_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/C--Installation-Specifications | Contracts / Commercial
C-1-Trenching-Specifications_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/C--Installation-Specifications | Contracts / Commercial
C-10-Overhead-Line-Specifications_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/C--Installation-Specifications | Contracts / Commercial
C-12-Erosion-Control-Technical-Specifications_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/C--Installation-Specifications | Contracts / Commercial
C-2-LC-System-Installation_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/C--Installation-Specifications | Contracts / Commercial
C-3-MV-System-Installation_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/C--Installation-Specifications | Contracts / Commercial
C-4-Grounding-System-Specification_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/C--Installation-Specifications | Contracts / Commercial
C-5-Civil-Work-Specifications_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/C--Installation-Specifications | Civil Design
C-6-Site-Preparations-Specifications_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/C--Installation-Specifications | Contracts / Commercial
C-7-Foundations-Specifications_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/C--Installation-Specifications | Contracts / Commercial
C-8-Access-and-Internal-Roads-Specifications_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/C--Installation-Specifications | Contracts / Commercial
C-9-Fencing-and-Gates-Specifications_Rev_0.pdf | PDF | Sales Automation/Client Data Transfer/Specifications/C--Installation-Specifications | Contracts / Commercial
Document_Log.pdf | PDF | Sales Automation/Client Data Transfer/Documents | Other
Endicott_1.0_04082024-SAT_48GCR-E-100.pdf | PDF | Sales Automation/Client Data Transfer/Documents/07-Engineering/Design-and-Engineering | Other
Endicott_O&M.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
Endicott_Town_Planner_approval_email_on_revised_fixed_tilt_site_plan_2.5.26.pdf | PDF | Sales Automation/Client Data Transfer/Documents/06-Permits/Local,-State-and-Federal-Permits-and-Approval | Interconnection
Pricing Template - December 2025 (DEI).xlsx | XLSX | Sales Automation/Proposal | Contracts / Commercial
Specification_Log_Current.pdf | PDF | Sales Automation/Client Data Transfer/Specifications | Contracts / Commercial
UGEI Exhibit Tracker.xlsx | XLSX | Sales Automation/EPC Contract | Contracts / Commercial

## Prompt & Instructions
Updated Prompt & Instructions
Prompt
Run a full project bid intake analysis on the uploaded ZIP folder and parse every document in full. This is a document-driven diligence review. You must read the contents of every relevant document and extract actual dates, statuses, responsibilities, approvals, conditions, and milestones from the text inside the documents. Do not rely only on file names, folder names, or superficial summaries. Core rules: 1. Parse the actual text of PDFs, Word files, spreadsheets, and image-based documents where readable. 2. Use actual document dates, issue dates, revision dates, application dates, approval dates, execution dates, and effective dates exactly as stated. 3. Do not infer approvals or completion unless documentary support is present. 4. If multiple documents conflict, identify the conflict and state which document is later, signed, executed, or otherwise more authoritative. 5. Cite the supporting document name for every substantive conclusion. 6. If a date, status, or responsibility is unclear, mark it as unclear rather than guessing. 7. Prefer final, signed, executed, and latest-authoritative documents over draft or superseded materials. 8. Treat spreadsheets as source documents and extract actual project quantities, bid assumptions, and checklist answers from them. 9. Where OCR or image-based review is required, use it only to supplement document parsing and identify the source file clearly. 10. The output must read like a real diligence memo and include estimating implications, not a light summary. Required output order: 1. Project Overview 2. Executive Summary 3. Full Document Inventory by Label Name 4. Estimating Summary / One-Page Overview 5. Detailed Permitting Summary 6. Permitting Timeline with Actual Dates 7. Permitting Deliverable Responsibilities 8. Permitting Issues and Risks 9. Interconnection Summary 10. Design Summary 11. Quantities Summary 12. Bid Template Answers 13. Risks and Missing Information Additional estimating instructions: - Add a one-page estimating summary to the Overview tab of the spreadsheet. - Include a design-basis comparison table if the package contains conflicting design bases. - Include a permitting status table with actual dates. - Include a concise list of estimating risks, available documents, and missing items. - Flag any mismatch between permitting basis, interconnection basis, design basis, and estimate basis. - Do not present a quantity as final if different quantities appear in different source documents. - Highlight missing construction-readiness items such as building permits, final SWPPP, access permits, field geotech, IFC drawings, and reconciled BOMs.
Instruction | Detail | Priority
Use actual text, not filenames | Do not summarize permitting, design, or interconnection from filenames alone. | Required
Inventory first | List every file with file name, type, path, and document category before drawing conclusions. | Required
Parse dates carefully | If a document contains multiple dates, identify what each date represents. | Required
Track responsibilities | For each permit or deliverable, identify the responsible party or mark Unclear – Requires Review. | Required
Separate status from requirement | A required deliverable is not complete unless the documents show approval, issuance, or execution. | Required
Quantities must be sourced | For MW, equipment counts, acreage, and line lengths, cite the exact document used. | Required
Conflicts must be explicit | Show both values when documents conflict and state that the design basis requires confirmation. | Required
Construction readiness matters | Call out missing building permit, electrical permit, SWPPP, highway permit, IFC drawings, and geotech if absent. | Required
Spreadsheet completion standard | Every field in the Bid Info Template must be marked Answered, Partial, Not Found, or Needs Review. | Required
Overview tab standard | The Overview tab should function as a one-page estimator handoff sheet. | Required
Overview tab updated to mirror the uploaded estimator summary structure.